## Questions & Answers
RFI # | QUESTIONS | REF PARAGRAPH | DATE ENTERED | DATE SUBMITTED | RESPONSE DATE | RESPONSE
1 | Please confirm that no new exterior lighting is required in this SOW. |  |  |  |  | Exterior lighting requirements are not part of this SoW
2 | 1.2.G states that available drawings can be provided upon requirest. Please provide all as-built drawings for the project building. Structural components and MEP/utility locations/sizes are needed to price the scope of work. |  |  |  |  | Available as builts have been provided
3 | Clarify if current windows and doors in the building meet the specified wind load rating required. |  |  |  |  | Yes; Project does not require any windows or external personnel doors to be replaced.
4 | Please provide guidance on whether the lighting controls need to tie into a building management system. If so, what brand? |  |  |  |  | They do not need to tie into the buidling management system
5 | Confirm that FF&E is not included in this scope of work. |  |  |  |  | FF&E is not included in the SoW
6 | Please clarify if new Ultra-sensitive sensors are required in Room 113. |  |  |  |  | The sesnsors should meet Tyndall IFS as referenced in the SoW
7 | Please qualify the quantity of outlets and projectors to be used in all rooms. Reference 2.1.1.d, 2.1.1.e, 2.1.2.d, and 2.1.2.e. |  |  |  |  | There will be two projectors and two projector screens in each room. At least one receptacle should be installed to power the two projectors and one receptacle to power the two screens.
8 | Clarify where should the ground conductor connect to feed the ground bar? What size should the ground conductor be? |  |  |  |  | Designer of Record should determine solution in accordance with all applicable codes and regulations.
9 | Please clarify if item 2.1.6.d is in reference to the entire building, or just this room. Please clarify the intent for use and connection. |  |  |  |  | This requirement applies only to this room. The requirement is necessary to support engine maintenance training.
10 | Please clarify if item 2.1.7.a is in reference to the transformer for the main electrical service to the building, or a separate transformer feeding only this room. |  |  |  |  | Designer of Record will need to coordinate with GCEC to determine if existing can be utillized or updated to meet requirements or if new separate system will need to be installed as part of the project
11 | Please advise for item 2.1.7.b. Where are these items needed? What amperage for each circuit? What are the aperage requirements for the equipment? |  |  |  |  | Refer to additional documents provied: "Proposed FabFin Work Area (2)"
12 | Where is the electrical panel located for item 2.1.7.b? Please identify on a drawing. |  |  |  |  | Refer to as built drawings
13 | How much weight does the mezzanine need to support? |  |  |  |  | 100 psf
14 | Confirm that projectors and projector screens are to be provided and installed by the government. |  |  |  |  | The screens and projectors are not required as part of the SoW.
15 | Please provide any hazardous material survey that has been conducted on the facility |  |  |  |  | None are available
16 | Please clarify item 2.1.6.g existing door size. |  |  |  |  | Refer to as built drawings
17 | Clarify if government is to provide and install an air compressor for item 2.1.6.e. |  |  |  |  | Installed air compressor lines should tie into existing system already installed in building. Contractor will provied and install new lines, guages and moisture traps as per the SoW
16 | Please clarify wall construction and length of wall to be removed for item 2.1.5.a |  |  |  |  | The entire wall should be removed to create a single room. However, the Designer of Record should determine if this is feasible and provide options to install a door in the wall if the entire wall cannot be removed
17 | Confirm that government will remove and reinstall all furniture and equipment from rooms prior to construction. |  |  |  |  | The government will remove items from the room prior to construction
18 | Confirm if this will be a tax exempt project. |  |  |  |  | Project is not know to be tax exempt as provided by the government
19 | Please clarify floor manufacturer and series for item 2.1.2.a |  |  |  |  | Unknown; Cannot be provided
20 | Please identify on a drawing the locations for raised platforms. |  |  |  |  | Refer to drawings provided with as builts
21 | Please clarify contractor on-site personnel requirements. |  |  |  |  | Contractor on-site requirements outlined within clauses/provisions of contract and SOW/SOW appendix further clarifications can be added in pre-conference meetings.
22 | 2.1.4.e indicates each workstation will be fitted with a manifold with a 1/4" industrial style quick disconnect, a moisture trap, and a pressure regulator. Please confirm if this is Contractor Furnished Contractor Installed, Government Furnished Government Installed, or Government Furnished Contractor Installed |  |  |  |  | These items will be contractor furnished and contractor installed
23 | Please confirm that Siemens is not required for any HVAC BAS controls and is not required for FA/MNS. |  |  |  |  | Siemens is not required
24 | Confirm how many workstations are in room 107 for item 2.1.4.e |  |  |  |  | There will be two work stations
25 | Please confirm that no modifications to the existing HVAC systems are required, and no new HVAC system is required. |  |  |  |  | HVAC will be needed for the server room. Designer of Record will need to determine the size and installation. The Data Center will require colling to 154138 BTUS/h.
26 | Please confirm that no modifications to the existing fire alarm systems are required, and no new fire alarm system is required. |  |  |  |  | Fire suppression requirements are not part of this SoW
27 | Confirm that modifications to the existing fire suppression systems are not included in the scope of work, or a new fire suppression system is not required. |  |  |  |  | Fire suppression requirements are not part of this SoW
28 | Please confirm that no new emergency egress items or modifications to existing egress systems are required. |  |  |  |  | Egress items and modifications are not part of this SoW
29 | 1. Room 107 (EMT) – Existing roll up door to be removed and replaced with new roll up door with required 14 ft wide X 12 ft high opening. Based on the location of the existing exterior wall corner and the location of the existing interior overhead crane column, it does not seem feasible to obtain a 14 ft wide opening for a new door. Will the overhead crane be removed from room 107? Please confirm the dimensions for the new roll up door. |  |  |  |  | a. The crane will remain in the room. The new door will need to be 14 feet wide. The footprint of the crane can be adjusted to support the installation of the door. The Designer of Record will need to determine the appropriate solution.
30 | 1. Room T-14 (FIN) – Will the existing heavy machinery and equipment remain in place inside the room? Will it be moved prior to award? Can it be moved by the contractor? |  |  |  |  | a. The equipment will remain in place. However, some of it can be moved to facilitate new work.
31 | 1. Room T-15 - Will the existing heavy machinery and equipment remain in place inside the room? Will it be moved prior to award? Can it be moved by the contractor? |  |  |  |  | a. The equipment will be removed prior to the start of construction.
32 | • Rooms 101-105 and Room 106 o Install raised platform 12 inches high, 84 inches wide and the full width of the room. RFI: Does the GOV have a BOD or better description of what they are looking for here; is this pre-manufactured, something built out of light gauge or structural steel, load requirements, etc.? |  |  |  |  | Designer of Record should determine the best method to provide the raised instructor classroom. The flooring should be able to support 100 pounds per square foot. Raised instructor floor must allow access under the floor to install electrical and communications cabling.
33 | Replace existing lighting and controls. RFI: The lighting looks new, is this lighting not compatible and does the GOV want all this lighting replaced? |  |  |  |  | The lighting and/or lighting control systems in the classrooms should be replaced to meet the standards as required in the SoW Appendix A
34 | Room 107 (Outer Mold Line)
35 | Install wall mounted conduit, wiring and a 120 VAC duplex outlet at each student desk to provide power to each of the 12 student workstations. Provide an additional 4 outlets throughout the room. RFI: Can you provide layout of student workstations and location for four additional outlets? |  |  |  |  | Student workstations will be placed along the walls to provide 12 work benches, in groups of two, equally spaced along the South, West, and North walls. East wall will be the location of the instructor desk plus 3 other special purpose workstations. Each work station will be approximately 72” (L) x 36” (W) x 29.5” (H)
36 | [5 empty] | Outlets should be provided at each of the 12 student workstations, the instructor workstation, and 3 additional special purpose workstations. Utilize existing outlets to maximum extent possible or relocate using wall mounted conduit to provide electrical connections at each workstation. Each workstation will also require compressed air (in accordance with SoW Appendix A) and LAN connections.
37 | o Seal existing concrete floor with traffic rated epoxy. RFI: Existing flooring is VCT, are we to remove this and install Epoxy? |  |  |  |  | Yes
38 | Install emergency eye wash station and plumb to existing water and drain lines. |  |  |  |  | Locate in North East corner of room; Plumb to existing building potable water system.
39 | RFI: Where is this to be located?
40 | Install one base telephone receptacle in the room. RFI: Please provide location. |  |  |  |  | South East corner along eastern wall; Instructor desk will be located in this area
41 | Rooms T-35 and T-36 (Instructor Office)
42 | Install wall mounted conduit with wiring and Cat 6 cable to provide communications and power to 25 workstations. RFI: Please provide layout. |  |  |  |  | Designer of Record will need to determine best layout to provide equal space to all individuals within the combined office space of rooms T-35 and T-36 once the wall is removed between them. It will be general office space to be shared equally.
43 | Room 107 (Engine Maintenance Trainer)
44 | Install wall mounted conduit, Cat 6 cable and communications outlet at two locations in room. RFI: Please provide locations. |  |  |  |  | The outlets will be located in pairs (CAT 6 and Communications Outlet) on the North and South walls; Tables / Desks will be located approximately centered on each of the walls where the outlets will be located.
45 | Install emergency eye wash station and plumb to existing water and drain lines. RFI: Please provide location. |  |  |  |  | Replace existing eye wash / emergency shower in South West corner
46 | Seal seams and cracks in existing concrete floor and coat with traffic rated epoxy. RFI: Can you provide an estimated type/quantity to account for? |  |  |  |  | Install epoxy coating over entire floor, and seal seams and cracks. Epoxy coating should fuel and oil resistant
47 | Install wall mounted compressed air lines to provide compressed air at each of the two workstations. RFI: Please provide location. |  |  |  |  | Compressed air will be provided to the Tables / Desks centered on the North and South walls.
48 | Install one base telephone receptacle in the room. RFI: Please provide location. |  |  |  |  | Receptacle will be installed on North wall, centered to provide phone to desk.
49 | Room T-14 (FIN)
50 | Replace or upgrade existing transformer to provide required power as listed in line item b below. Coordinate with GCEC regarding any and all work to replace the transformer and provide the necessary power. RFI: Please provide GCEC POC for pricing. |  |  |  |  | Bill Kuehl, william.kuehl.1@us.af.mil
51 | Install wiring and provide power to support industrial equipment located in lab per end user requirements: 208V 1PH, 208V 3PH, 208/230V, 220V, 415V. RFI: Please provide equipment layout with voltage requirements. |  |  |  |  | PDF “Proposed FabFin Work Area (2)” provides approximate locations for power requirements.
52 | Install mezzanine system to provide 900 sf of raised storage space above the floor. Floor to the bottom of the mezzanine height shall be at least 8 feet to allow full use of the area under the mezzanine. RFI: Please provide location. |  |  |  |  | North East Corner of the room
53 | Install emergency eye wash station and plumb to existing water and drain lines. RFI: Where is this to be located? |  |  |  |  | Replace existing eye wash / emergency shower in North West corner
54 | Install one base telephone receptacle in the room. RFI: Please provide location. |  |  |  |  | Install receptacle / line under mezzanine
55 | Room T-15
56 | o Install ventilation system to remove exhaust from welding operations. RFI: Can you provide a layout of where this is to be installed? |  |  |  |  | § Install centrally located exhaust system that vents air to the outside. Provide system with adjustable vacuum hose / hood that can be adjusted / located as required to support work requirement.
57 | o Install emergency eye wash station. RFI: Where is this to be located? |  |  |  |  | § North East Corner of room
58 | General
59 | Can you provide Record Drawings for these areas |  |  |  |  |  Refer to provided as builts
60 | Can you provide layouts for all rooms being renovated for desks, equipment, etc.? |  |  |  |  | FFE (desks / equipment) will be installed separately. All work for communications, electrical, and other lines should be based on the descriptions in the SoW Appendix A.
61 | · the SOW and Solicitation give a duration of 270 days while the RFP states 280 days. Can the base clarify which is accurate? |  |  |  |  | o 280
62 | · Can the as built drawings for Bldg 549 be provided uploaded to beta.sam for contractor and designer reference? |  |  |  |  | o Yes
63 | Do all outlets that are to be provided to each desk have to have a dedicated circuit? If so, can a sub-panel be set for each individual room? |  |  |  |  | o Use the existing circuits in the room and relocate the existing outlets to provide power as stated for each room in the SoW Appendix A. Exact locations of the outlets will be determined by the Designer of Record based on the final layout of the rooms. Outlets will be relocated from wall to under the raised floor and will not extend more than 5 feet from wall. EML Rooms were previously used as classrooms and will be used in the same manner following completion of this project.
64 | ow many projectors will need to be located in each classroom 101-106? |  |  |  |  | Two
65 | Where is the mezzanine to be located in room FIN? |  |  |  |  | North East corner
66 | Will there need to be lighting installed under the mezzanine so that work can be performed underneath? |  |  |  |  | Yes
67 | • In the Outer Mold Line, the SOW states to seal the existing floor with epoxy. There is currently VCT tile in place that would need to be removed. Has there been an asbestos test for this tile and/or mastic adhesive? |  |  |  |  | No
68 | Is there existing lightning protection on the building? If so, do we need to tie-in to it? |  |  |  |  | Yes there is existing lightning protection. Yes, any new electrical work should be tied into the system if the Designer of Record determines it must be, and any modifications to the existing electrical system must remain tied into the lightning protection system.
69 | In the Data Center, what size of main circuit breaker disconnect is required? |  |  |  |  | The power requirements for the data center are 70 kVA, 480 VAC, 125 Amps, 3 phase, 60 Hz
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100