8.3.2026 - UPDATE
Question & Answer
Questions and clarifications about the project
The question submission deadline has passed. No more questions can be submitted.
1. drawings Jul 14 2026 at 2:01 PM
· 
Anonymous Jul 14 2026 at 2:01 PM
User information is private
The drawings for this project that have been provided have been reduced to 8.5 x 11 size. We need full size drawings . Please provide updated drawings
· 
Jul 15 2026 at 12:27 PM
Escambia County
Please see Official Notice #1: Paradise Beach Bid Set Drawings 07.10.2026.
2. No subject Jul 15 2026 at 12:54 PM
· 
Anonymous Jul 15 2026 at 12:54 PM
User information is private
Bigger plans
· 
Jul 15 2026 at 12:59 PM
Escambia County
Please see Official Notice #1: Paradise Beach Bid Set Drawings 07.10.2026.
3. No subject Jul 15 2026 at 1:18 PM
· 
Anonymous Jul 15 2026 at 1:18 PM
User information is private
Can the County please confirm whether audiovisual, conferencing, training room, digital signage, emergency operations, or other low-voltage technology systems are included within the scope of the Paradise Beach Fire Station 20 project? If so, are these systems included in the base bid documents, and should interested technology integration firms coordinate directly with the bidding General Contractor(s) regarding those scopes?
· 
Jul 20 2026 at 10:42 AM
Escambia County
Certain specialized low-voltage systems are not included within the base bid scope and will be provided through a separate allowance utilizing a County pre-selected technology integration vendor. These systems include, but are not limited to, audiovisual equipment, security surveillance cameras, access control systems, fire station alerting and ramp-up systems, and other specialized electronic security and communications technologies. The General Contractor shall coordinate with the County's designated technology integration vendor during construction as required by the Contract Documents to provide the necessary infrastructure, pathways, rough-ins, power, backing, and other preparatory work necessary to support the installation of these systems.
4. Specification Section 221111 Jul 15 2026 at 2:37 PM
· 
Anonymous Jul 15 2026 at 2:37 PM
User information is private
Specification section 221111 is not listed in the index. This words in this section of the specifications are jumbled and incoherent. Please provide a corrected version. 
· 
Jul 20 2026 at 10:42 AM
Escambia County
The County has reviewed the Project Manual and was unable to locate Specification Section 221111 referenced in this RFI. Based on our review, no such specification section is included in the issued Bid Documents.
5. Quartz Countertops Jul 17 2026 at 10:09 AM
· 
Joshua Owens Jul 17 2026 at 10:09 AM
GSI Construction Corporation, Inc
Your information is only visible to you
Several of the details on Drawing A401 show Quartz countertops. There does not appear to be any specs. Can the brand and color for the quartz be provided? 
· 
Jul 20 2026 at 11:30 AM
Escambia County
Please refer to Drawing Sheet A106, where the countertop finish is identified. The Contract Documents specify a solid surface countertop, identified as Corian Neutral Aggregate, and not a quartz countertop.
6. Directional Compass on MEP Floor Plans Jul 17 2026 at 11:23 AM
· 
Anonymous Jul 17 2026 at 11:23 AM
User information is private
it appears the directional compass shown on the plumbing, mechanical, and electrical floor plans is inconsistent with the architectural drawings.
· 
Jul 20 2026 at 11:30 AM
Escambia County
The discrepancy has been reviewed and is confirmed to be a drafting error resulting from the reuse of a previous project template. The directional north arrow shown on the plumbing, mechanical, and electrical drawings is incorrect. This item will be corrected in a forthcoming Addendum. The architectural drawings shall govern with respect to the project orientation until the corrected drawings are issued.
7. 6' Retainage Pond Fence Jul 17 2026 at 12:12 PM
· 
Joshua Owens Jul 17 2026 at 12:12 PM
GSI Construction Corporation, Inc
Your information is only visible to you
Can a spec be provided for the retention pond fencing?
· 
Jul 20 2026 at 11:30 AM
Escambia County
Yes. A specification section for the stormwater retention pond fencing will be issued in a forthcoming Addendum. The Addendum will also include a revised fencing detail identifying the required green vinyl-coated chain-link fence.
8. Decorative Metal Fence & Gates Jul 17 2026 at 12:14 PM
· 
Joshua Owens Jul 17 2026 at 12:14 PM
GSI Construction Corporation, Inc
Your information is only visible to you
Can Stephens Pipe and Steel be added to the Specification Section 323119 Decorative Metal Fence and Gates as an approved fabricator?
· 
Jul 20 2026 at 11:30 AM
Escambia County
Yes. Stephens Pipe & Steel will be added as an approved manufacturer for Specification Section 323119 – Decorative Metal Fences and Gates in forthcoming Addendum No. 1.
9. Spec Section 230000 HVAC General Jul 17 2026 at 2:58 PM
· 
Anonymous Jul 17 2026 at 2:58 PM
User information is private
Reviewing spec section 230000, we found that the text is scrambled and unreadable throughout the section, preventing a complete review of the specification requirements. Please provide a corrected, legible copy of Specification Section 230000.
· 
Jul 20 2026 at 11:30 AM
Escambia County
The County and Design Team have reviewed the issue and confirmed that Specification Section 23 0000 was inadvertently corrupted during the assembly of the Project Manual, resulting in portions of the text being unreadable. A complete, corrected, and legible version of Specification Section 23 0000 will be issued as part of a forthcoming Addendum.
10. PEMB Jul 20 2026 at 9:28 AM
· 
Anonymous Jul 20 2026 at 9:28 AM
User information is private
How can we submit a substitution request to add All Metal Building as an approved manufacturer? 
· 
Jul 21 2026 at 8:07 AM
Escambia County
Requests to add manufacturers as approved equals or to request substitutions shall be submitted in writing through the Request for Information (RFI) process during the bidding period.
11. Sealed Concrete Jul 20 2026 at 9:58 AM
· 
Joshua Owens Jul 20 2026 at 9:58 AM
GSI Construction Corporation, Inc
Your information is only visible to you
The plans show sikagard 707w for apparatus bay floor sealer. A subcontractor is warning that this product is not advisable for an aggressive apparatus bay floor sealer. Instead, they are suggesting a skiafloor systems 264-315n - can the architect confirm which product is better suited?
· 
Jul 23 2026 at 12:00 PM
Escambia County
This item will be addressed in an upcoming Addendum.
12. PEMB Foundation Jul 20 2026 at 10:07 AM
· 
Joshua Owens Jul 20 2026 at 10:07 AM
GSI Construction Corporation, Inc
Your information is only visible to you
Foundation will need redesign after PEMB manufacture submits their shop drawings and calculations. Please confirm the Engineer of record will provide this redesign. 
· 
Jul 21 2026 at 8:12 AM
Escambia County
Should those calculations require revisions to the foundation design to accommodate the selected PEMB system, the Engineer of Record will provide the necessary foundation revisions.
13. Specification Section 221111 (again) Jul 20 2026 at 10:50 AM
· 
Anonymous Jul 20 2026 at 10:50 AM
User information is private
Specification section 221111 is included in the specifications following section 211300 - fire Protection Sprinkler Systems. It is not listed in the index. The words in this section of the specifications are jumbled and incoherent. Please provide a corrected version. 
· 
Jul 20 2026 at 12:06 PM
Escambia County
Please see Official Notice #3
14. Approved Storefront manufacturers & Products Jul 20 2026 at 1:25 PM
· 
Joshua Owens Jul 20 2026 at 1:25 PM
GSI Construction Corporation, Inc
Your information is only visible to you
Spec section 08411, Part 2 - Products, 2.01.A. lists several approved manufacturers that the contractor is to use. A Subcontractor is requesting that Coral Architectural Products be an approved manufacturer and that their FL550T Hurricane-Resistant Storefront System be an approved product - More information be provided. 
· 
Jul 21 2026 at 8:56 AM
Escambia County
Yes. Coral Architectural Products will be added as an approved manufacturer for Specification Section 08 4113 - Aluminum Storefront in forthcoming Addendum No. 1.
15. Budget Jul 20 2026 at 2:21 PM
· 
Anonymous Jul 20 2026 at 2:21 PM
User information is private
Is there a budget or architects estimated cost for this project? 
· 
Jul 23 2026 at 12:00 PM
Escambia County
Escambia County has appropriated funding for this project and intends to award a contract subject to receipt of responsive bids, Board approval, and available funding.
16. Request for Approval of PEMB Manufacturer Jul 20 2026 at 2:23 PM
· 
Anonymous Jul 20 2026 at 2:23 PM
User information is private
We would like to request that Pinnacle Structures be considered an approved Pre-Engineered Metal Building manufacturer for this project.
· 
Jul 21 2026 at 8:56 AM
Escambia County
Pinnacle Structures may be added as an approved Pre-Engineered Metal Building (PEMB) manufacturer in a forthcoming Addendum, provided the proposed building system fully complies with all requirements of the Contract Documents, including the specified design criteria, structural performance, wind load requirements, materials, finishes, warranties, and all other applicable project specifications.
17. Bollards Jul 20 2026 at 2:27 PM
· 
Anonymous Jul 20 2026 at 2:27 PM
User information is private
Civil and Structural note bollards are 6" diameter std pipe. Architectural plans note as 4" diameter std. pipe. Which is correct?
· 
Jul 21 2026 at 8:56 AM
Escambia County
The Civil drawings are correct. The required bollards shall be 6-inch diameter standard steel pipe, as indicated on those drawings. The 4-inch diameter bollard note shown on the Architectural drawings is incorrect. The Architectural drawings will be revised to reflect the correct 6-inch diameter bollards in Addendum No. 1. Until the Addendum is issued, bidders shall base their bids on the 6-inch diameter requirement.
18. Bollards Jul 20 2026 at 2:28 PM
· 
Anonymous Jul 20 2026 at 2:28 PM
User information is private
Structural plans S201 show bollards @ detail 9 with a base plate. Detail 10 shows typical type bollard. Which is correct? If base plate & anchors are required, please provide plate size and anchor size.
· 
Jul 21 2026 at 8:56 AM
Escambia County
The Structural bollard details shown on Drawing S201 shall be omitted. The Civil bollard detail is the governing detail for this project and shall be used for bidding and construction. The conflicting Structural details will be removed from the Contract Documents in a forthcoming Addendum to eliminate the discrepancy.
19. Project Budget/Estimate Jul 20 2026 at 2:29 PM
· 
Anonymous Jul 20 2026 at 2:29 PM
User information is private
What is the project budget or engineers estimate? This helps us when ordering a bid bond.
· 
Jul 23 2026 at 12:00 PM
Escambia County
Escambia County has appropriated funding for this project and intends to award a contract subject to receipt of responsive bids, Board approval, and available funding.
20. C202 - West side parking Jul 20 2026 at 2:29 PM
· 
Anonymous Jul 20 2026 at 2:29 PM
User information is private
On sheet C202 - West side parking there are (5) black dots shown with no notation. Are these bollards? 
· 
Jul 21 2026 at 8:56 AM
Escambia County
Yes. The five (5) unlabeled symbols shown on the west side parking area of Drawing C202 represent bollards, consistent with the bollards identified and labeled on Drawing C201.
21. Guard rail / gate Jul 20 2026 at 2:30 PM
· 
Anonymous Jul 20 2026 at 2:30 PM
User information is private
Detail 2 / Sheet A504 shows approximately 6 LF of Guard Rail & Gate. Detail 1 / Sheet A104 shows / noted multiple sections with rail. Which is correct?
· 
Jul 21 2026 at 8:56 AM
Escambia County
The guardrail and gate configuration shown on Detail 2, Drawing A504 is correct and shall govern. The note shown on Drawing A104 indicating additional guardrail sections is incorrect and will be omitted.
22. Permit Jul 20 2026 at 2:49 PM
· 
Anonymous Jul 20 2026 at 2:49 PM
User information is private
Provide permit cost
· Question is acknowledged
23. Flag Pole Manufacturer Approval Jul 20 2026 at 3:42 PM
· 
Anonymous Jul 20 2026 at 3:42 PM
User information is private
We would like to request that Concord American Flagpole be considered an approved manufacturer for this project.
· 
Jul 23 2026 at 12:00 PM
Escambia County
Concord American Flagpole will be added as an approved manufacturer
24. Fees Jul 21 2026 at 8:39 AM
· 
Anonymous Jul 21 2026 at 8:39 AM
User information is private
Please confirm which utility tap fees, impact fees, and utility company charges are Owner-paid versus Contractor-paid.
· 
Jul 23 2026 at 12:00 PM
Escambia County
This information will be addressed by Addendum.
25. Generator Package Jul 21 2026 at 8:41 AM
· 
Anonymous Jul 21 2026 at 8:41 AM
User information is private
Please confirm the standby generator package is complete, including: fuel tank size weather enclosure load bank requirements sound attenuation startup and commissioning monitoring requirements fuel polishing (if applicable) The specifications clearly include a diesel generator and transfer switches but these items often generate change orders if not clarified
· 
Jul 23 2026 at 12:00 PM
Escambia County
This information will be addressed by Addendum.
26. Brick Selection Jul 21 2026 at 8:42 AM
· 
Anonymous Jul 21 2026 at 8:42 AM
User information is private
Confirm final brick manufacturer, color selections, mortar colors, and whether equal manufacturers are acceptable.
· 
Jul 23 2026 at 12:00 PM
Escambia County
For bidding purposes, Contractors shall base their bids on a cost of $650.00 per thousand for brick material only with standard gray mortar, as specified. The final brick manufacturer, color, and texture will be selected by the County during the construction phase. 
27. Typical Unit Prices Jul 21 2026 at 8:46 AM
· 
Anonymous Jul 21 2026 at 8:46 AM
User information is private
If unsuitable material, groundwater, or additional undercut beyond that identified in the geotechnical report is encountered, will additional excavation, borrow material, disposal, and replacement be compensated by change order? Or should we expect to see a unit price table to be included in an upcoming addenda?
· 
Jul 23 2026 at 12:00 PM
Escambia County
If unsuitable soils, groundwater, or other subsurface conditions materially differing from those indicated in the Contract Documents are encountered during construction, the Contractor shall immediately notify the County and Engineer of Record in accordance with the Contract Documents and shall not proceed with corrective work until directed. Upon verification by the County and Engineer of Record, any additional excavation, undercut, borrow material, disposal, and replacement required as a result of the differing site conditions will be evaluated and, if determined to be outside the Contractor's scope of work, may be addressed through a Change Order in accordance with the Contract.
28. Fire Suppression Jul 21 2026 at 8:57 AM
· 
Joshua Owens Jul 21 2026 at 8:57 AM
GSI Construction Corporation, Inc
Your information is only visible to you
Good afternoon, FP101 states apparatus bay to have Dry Pipe Sprinkler System. M101 shows infrared heaters in the apparatus bay. If the apparatus bay is heated there would not be a need for a Dry System?
· 
Jul 23 2026 at 12:00 PM
Escambia County
This information will be addressed by Addendum.
29. Fencing Spec Jul 21 2026 at 9:00 AM
· 
Joshua Owens Jul 21 2026 at 9:00 AM
GSI Construction Corporation, Inc
Your information is only visible to you
On the specs for the pickets in fencing and gate. 2.4 A. “fences made from steel tubing and shapes" The call out on 2.4 E. calls for ¾” square bar pickets. Just want to confirm they do want solid bar on the pickets and not tubing. 
· 
Jul 23 2026 at 12:00 PM
Escambia County
Square bar pickets or tubing will be acceptable.
30. Fees Jul 21 2026 at 9:08 AM
· 
Anonymous Jul 21 2026 at 9:08 AM
User information is private
Verify that the water, sewer, tap and impact fees will be paid by the owner.
· 
Jul 23 2026 at 12:00 PM
Escambia County
This information will be addressed by Addendum.
31. Permit Jul 21 2026 at 9:08 AM
· 
Anonymous Jul 21 2026 at 9:08 AM
User information is private
Provide permit allowance.
· Question is acknowledged
32. Insurance Jul 21 2026 at 10:04 AM
· 
Anonymous Jul 21 2026 at 10:04 AM
User information is private
Confirm that the Builders Risk Insurance will be provided by the owner.
· 
Jul 23 2026 at 12:00 PM
Escambia County
Yes, Builders Risk Insurance will be provided by the County for this project. 
33. Request for Approval of PEMB Manufacturer Jul 21 2026 at 11:44 AM
· 
Anonymous Jul 21 2026 at 11:44 AM
User information is private
We would like to request that All Metal Buildings be considered an approved Pre-Engineered Metal Building manufacturer for this project.
· 
Jul 23 2026 at 12:00 PM
Escambia County
All Metal Building is approved as long as they meet all requirements of the original specification.
34. Telecomm Jul 21 2026 at 2:18 PM
· 
Joshua Owens Jul 21 2026 at 2:18 PM
GSI Construction Corporation, Inc
Your information is only visible to you
• Please confirm whether the paging-system cabling is to be furnished and installed by the Division 27 contractor, Division 26 contractor, or another contractor. If the system equipment will be owner-furnished, please identify which components are owner-furnished and clarify who is responsible for installation, programming, testing, and final commissioning. • If a complete paging system is required, please provide the system specifications, including the basis-of-design manufacturer, amplifier and control equipment, speaker types, volume controls, cabling requirements, system zoning, equipment locations, and connection requirements. • The contract documents indicate that the cameras and associated video equipment are owner-furnished, while the Division 27 contractor is responsible for the associated horizontal cabling. However, it is not clear who is responsible for physically mounting the owner-furnished cameras. • Please clarify who is responsible for furnishing and installing the Atlas monitor mounts and for mounting the flat-panel displays. 
· 
Jul 24 2026 at 4:13 PM
Escambia County
• We don’t show any horizontal cabling for a paging-system. The language on T-001 will be revised to avoid confusion with the special systems work but the General Contractor is responsible for all Division 27 requirements per the Specifications and the drawings. Refer to Specifications section 270000. The responsibilities note on T-001 is intended to delineate the responsibilities of the different trades. • Not required. An allowance will be issued by Addendum that will be included in the bid to handle systems costs. • The mounting of the cameras will be by the owner, through a separate contract. • Per sheet A103, these are to be provided by Owner. Installation and hook up is by General Contractor.
35. Stainless Steel Cabinets Jul 22 2026 at 9:27 AM
· 
Anonymous Jul 22 2026 at 9:27 AM
User information is private
Reference Sheet A402. Provide specification and manufacturers for stainless steel cabinets, tops and splashes.
· 
Jul 23 2026 at 12:00 PM
Escambia County
Cabinets, tops, and splashes to be by Advance Tabco, or approved equal.
36. Plastic Laminate Lockers Jul 22 2026 at 9:28 AM
· 
Anonymous Jul 22 2026 at 9:28 AM
User information is private
Reference Sheet A401. Provide specifications and manufacturers for plastic laminate lockers. 
· 
Jul 23 2026 at 12:00 PM
Escambia County
Plastic laminate lockers are to be custom built by millwork supplier on job.
37. Equipment / Person Desk Jul 22 2026 at 9:31 AM
· 
Anonymous Jul 22 2026 at 9:31 AM
User information is private
Reference Sheet A103 Equipment Schedule items 050 and 036 which are OF/OI. Reference elevation 104A/A401 Dorm room which indicates millwork. Clarify. 
· 
Jul 23 2026 at 12:00 PM
Escambia County
A103 Equipment Schedule is correct, Owner furnished and installed. A401 will be clarified by Addendum.
38. Access Control Jul 22 2026 at 9:32 AM
· 
Anonymous Jul 22 2026 at 9:32 AM
User information is private
Provide contractors scope of work for door access control. Provide raceway plan if a central control panel is utilized. Nothing indicated on E121 systems.
· 
Jul 23 2026 at 12:00 PM
Escambia County
Contractor to provide all information as required by door hardware specification. Power supply and low voltage wiring for these doors will be provided for in Bid by a Systems Allowance that will be issued by Addendum.
39. Electrical Cord Reels Jul 22 2026 at 9:33 AM
· 
Anonymous Jul 22 2026 at 9:33 AM
User information is private
Reference A103 and E111. Item 065 Electrical Cord Reels not indicated on electrical plan. Clarify.
· 
Jul 23 2026 at 12:00 PM
Escambia County
Electrical cord reels will be added to electrical plan by Addendum.
40. Rapelling Anchor Jul 22 2026 at 9:34 AM
· 
Anonymous Jul 22 2026 at 9:34 AM
User information is private
Reference Item 037 Rapelling Anchor by Fire Facilities. These are engineered anchors designed for their training facilities. Structure must be designed accordingly. 
· 
Jul 23 2026 at 12:00 PM
Escambia County
Noted, provide anchors in Bid price.
41. Equipment Schedule - Item 13 Jul 22 2026 at 9:35 AM
· 
Anonymous Jul 22 2026 at 9:35 AM
User information is private
Reference Sheet A103. Equipment Schedule item 13 is FBO. Contractor provided equipment schedule 13 is FBGC. Clarify. 
· 
Jul 23 2026 at 12:00 PM
Escambia County
This item will be Owner furnish, and can be omitted from the Contractor's provided equipment list.
42. Key Cabinet Jul 22 2026 at 9:45 AM
· 
Anonymous Jul 22 2026 at 9:45 AM
User information is private
Provide specification for key cabinet.
· 
Jul 23 2026 at 12:00 PM
Escambia County
Indicated on sheet A103.
43. Wall Panels Jul 22 2026 at 9:45 AM
· 
Anonymous Jul 22 2026 at 9:45 AM
User information is private
Provide specification for wall panels - indicating thickness, fabric, density, etc.
· 
Jul 23 2026 at 12:00 PM
Escambia County
Panels are specified on sheet A801.
44. Mirrors Jul 22 2026 at 9:47 AM
· 
Anonymous Jul 22 2026 at 9:47 AM
User information is private
Reference Sheet A103 - Item 44 - Mirrors. Provide elevation of East wall indicating size of mirrors.
· 
Jul 23 2026 at 12:00 PM
Escambia County
On the East wall, there will be (3) 3-FT X 5-FT mirrors. 
45. Room Signs Jul 22 2026 at 9:47 AM
· 
Anonymous Jul 22 2026 at 9:47 AM
User information is private
Advise is room signs will be required for this project. If so, provide signage plan and detail of sign.
· 
Jul 23 2026 at 12:00 PM
Escambia County
Exterior signs are shown on sheet A201. Interior signs will be issued by Addendum.
46. Item 17 - Wall Rack Jul 22 2026 at 9:49 AM
· 
Anonymous Jul 22 2026 at 9:49 AM
User information is private
Reference Sheet A103 Item 17 Wall Rack. There are 2 indicated on the plans. Contractors Equipment schedule reference see detail 8/A506. This indicates a millwork ledge. Advise.
· 
Jul 23 2026 at 12:00 PM
Escambia County
Both are correct. Detail 8/A506 shows a millwork ledge with prefab hooks. This is a custom built wall rack.
47. Question 3 Response Jul 22 2026 at 1:00 PM
· 
Anonymous Jul 22 2026 at 1:00 PM
User information is private
Reference Question 3 answer. Without plans and specification of the Owner provided systems, there is no way for the contractor to provide pricing in his bid to provide the infrastructure for these systems. Suggest an allowance. Advise. 
· 
Jul 23 2026 at 12:00 PM
Escambia County
An allowance will be issued by Addendum.
48. Pest Control Jul 22 2026 at 3:01 PM
· 
Joshua Owens Jul 22 2026 at 3:01 PM
GSI Construction Corporation, Inc
Your information is only visible to you
1. Section 06 1053 references site-applied borate treatment to wood framing under the Termite Control specification. However, the project appears to be primarily metal-framed, and Section 02 3610 addresses soil treatment only. Please confirm whether field-applied borate treatment is required on any wood components. If required, please identify the specific wood materials and locations to be treated, the required product and application rate, and any warranty or submittal requirements. 2. Section 01 5000, Temporary Facilities and Controls, requires the Contractor to engage a pest-control service to perform extermination and control procedures at regular intervals during construction and to provide a final pest-control inspection report. Please clarify the required service frequency, anticipated duration of service, and areas to be included, such as the building interior, building perimeter, contractor trailers, dumpsters, storage areas, and the overall project site. Please also confirm whether routine callback service is expected to be included in the base bid and whether any specific pests, treatment methods, monitoring devices, or reporting format are required. 
· 
Jul 23 2026 at 12:00 PM
Escambia County
1. Treatment of wood components will not be required on this job. 2. Once building is enclosed, provide spray insect treatment once per month until project is complete.
49. ADA Chair Lift Jul 22 2026 at 3:34 PM
· 
Joshua Owens Jul 22 2026 at 3:34 PM
GSI Construction Corporation, Inc
Your information is only visible to you
Is there a spec, or basis of design, for the proposed ADA Chair Lift at Bldg A?
· 
Jul 23 2026 at 12:00 PM
Escambia County
None is required.
50. Telecomm Jul 23 2026 at 10:13 AM
· 
Joshua Owens Jul 23 2026 at 10:13 AM
GSI Construction Corporation, Inc
Your information is only visible to you
1. Sheet T101, detail 3 depicts 12” perimeter cable tray. Sheet T502, detail 9 depicts 18” perimeter ladder rack. Please advise ladder tray width for Telecom Room. 2. Above drawings notes appear to conflict with specifications 271300 page 7 of 15, B8, as the racks are floor mounted and connected to the overhead cable tray already. Please advise. 3. Please advise cable color for Cat 6A cable. 4. Jack color for Cat 6 WAO is depicted as white to match faceplate. Please advise jack color for WAP locations. 5. Sheet T001, detail 1 data riser diagram shows the fiber optic enclosure. Please advise if adapters or splice cassettes are required. If so, please advise fiber count, single mode or multi-mode, and connector type. 6. Sheet T501, detail 7 appears to depict option to install 3” 3-cell fiber mesh innerduct. Please advise if it is acceptable to install 3 each, 3” 3-cell fiber mesh innerduct in the one 4” conduit as opposed to the corrugated innerduct. 7. Please advise quantity, color, and length of Cat 6 and Cat 6A patch cords required and to be included in the sign off sheet. 8. Please advise quantity, color, length, connector type(s), and if single mode or multi-mode or both, to be included in the sign off sheet. 
· 
Aug 3 2026 at 12:53 PM
Escambia County
1. Provide 12” ladder rack with 1” side channels. See upcoming Revision 2. 2. Provide rack elevation kit to secure rack to 12” ladder rack. 3. Provide cable color per the Data Riser Diagram on Sheet T001. 4. Provide white to match faceplate. 5. Connectors and ca shall be coordinated with ISP. 6. Corrugated innerduct is not required. Provide 3” Cell fiber mesh innerduct per detail Sheet E501 detail 7. 7. Provide one patch cord per network drop. Length as required to route cable through cable managers from patch panel to switch. Color shall match the horizontal cables. 8. Provide patch cords in accordance with Specification Section 261300.2.3. 
51. Sectional Overhead Doors Jul 23 2026 at 1:08 PM
· 
Joshua Owens Jul 23 2026 at 1:08 PM
GSI Construction Corporation, Inc
Your information is only visible to you
Does Door Type J require “Water Infiltration Resistance” per ASTM E331 & ASTM E547?
· Question is acknowledged
52. Substitution Request Jul 23 2026 at 1:14 PM
· 
Joshua Owens Jul 23 2026 at 1:14 PM
GSI Construction Corporation, Inc
Your information is only visible to you
Glass Garage Doors & Entry Systems would like be recognized as an approved vender. They can provide their NFRC verification, as Specified in 08 36 13, Sectional Overhead Doors. They have requested that all other venders ensure that they comply with the N.F.R.C. for the Air Infiltration, ASTM E283, Florida Energy Code Compliant. Being tested and having an Air Infiltration Rating IS NOT the same as being N.F.R.C. Rated. They encourage the GC and Architect of Record to visit the NRFC website directly to verify certification and label requirements according to the N.F.R.C. Can Glass Garage Doors & Entry Systems be recognized as approved venders for this project?
· 
Jul 27 2026 at 3:52 PM
Escambia County
Glass Garage Doors & Entry Systems is approved as a vendor, as long as all requirements of the original specs are met.
53. Door J Jul 24 2026 at 10:53 AM
· 
Anonymous Jul 24 2026 at 10:53 AM
User information is private
We are requesting a product substitution for Door type J. bp Glass Garage Doors & Entry Systems 1511 W. 2nd Street Pomona CA 91766 (626) 442-1716
· 
Jul 27 2026 at 3:52 PM
Escambia County
Glass Garage Doors & Entry Systems is approved as a vendor, as long as all requirements of the original specs are met.
54. Landscape Jul 24 2026 at 12:00 PM
· 
Anonymous Jul 24 2026 at 12:00 PM
User information is private
Plans show an irrigation well, are we supplying irrigation as well? Please supply desired sod boundary 
· 
Jul 27 2026 at 3:52 PM
Escambia County
Irrigation is to be supplied. Additional information on this is to be included by Addendum.
55. RFI Jul 24 2026 at 2:41 PM
· 
Anonymous Jul 24 2026 at 2:41 PM
User information is private
RFI-010 Doors / Hardware 08 7100 / E/T sheets Confirm electrified hardware, access control, keying, cores and security integration responsibilities. The Q&A states that access control and other specialized security/technology systems are not in the normal base-bid trade scope. They will be handled through a separate allowance using the County’s pre-selected technology integration vendor, with the GC responsible for coordination. Keep the RFI open only for electrified door hardware, power transfers, door contacts, locking hardware, keying, permanent cores, and the exact interface/scope split between Division 08, electrical, and the County vendor. 
· 
Jul 27 2026 at 3:52 PM
Escambia County
The door hardware required to handle this need is included in the Door Hardware Specification and should be included in the Bid price. The allowance will provide additional funds to handle adding the wiring and items that are listed by Owner in the Door Hardware Spec.
56. No subject Jul 24 2026 at 2:42 PM
· 
Anonymous Jul 24 2026 at 2:42 PM
User information is private
RFI-011 Roofing / PEMB 07 / 13 / A801 Confirm responsibility for metal roof/wall panels, insulation, weather barrier, flashing, gutters/downspouts and warranty terms. 
· 
Jul 27 2026 at 3:52 PM
Escambia County
Installation price is to be included in Bid. Owner may elect to purchase metal building direct. These items will be addressed by Addendum.
57. RFI Jul 24 2026 at 2:44 PM
· 
Anonymous Jul 24 2026 at 2:44 PM
User information is private
RFI-012 Fire Protection 21 / FP / C-401 Confirm underground fire service limits, fire pump requirements if any and fire alarm monitoring interfaces. 
· 
Aug 3 2026 at 12:53 PM
Escambia County
Extents of underground Fire Protection piping is shown on sheets C401 UTILITY PLAN and FP101 FLOOR PLANS – FIRE PROTECTION. No fire pump is required. Extents of fire alarm monitoring is indicated on sheet E010 SITE PLAN and E121 FLOOR PLANS – FIRE ALARM.
58. RFI Jul 24 2026 at 2:44 PM
· 
Anonymous Jul 24 2026 at 2:44 PM
User information is private
RFI-013 HVAC 23 / M schedules / M701 Confirm HVAC equipment substitutions, controls integration and dehumidification sequence requirements. 
· 
Aug 3 2026 at 12:53 PM
Escambia County
Refer to project specifications for HVAC equipment substitutions. See M701 for controls integration and dehumidification sequence requirements. 
59. RFI Jul 24 2026 at 2:45 PM
· 
Anonymous Jul 24 2026 at 2:45 PM
User information is private
RFI-014 Plumbing / Gas 22 1700 / P111 Confirm gas utility service scope, meter/regulator responsibility and service pressures. 
· 
Aug 3 2026 at 12:54 PM
Escambia County
Site Utilities contractor to coordinate provision of meter and first stage regulator with utility company. Plumbing contractor to provide second stage regulator for 0.5 PSI (14” WC) building pressure and building shutoff valve. Meter requirements as follows: Demand: 1054 CFH Max Pressure Drop: 0.5” WC Building Pressure: 0.5 PSI
60. RFI Jul 24 2026 at 2:46 PM
· 
Anonymous Jul 24 2026 at 2:46 PM
User information is private
RFI-015 Finishes 09 9100 / A106 Confirm apparatus bay floor coating system, slab moisture testing/mitigation responsibility and finish selections. 
· 
Jul 27 2026 at 3:52 PM
Escambia County
Addition information for bay floor coating system is to be provided by Addendum.
61. Stainless steel table Jul 24 2026 at 3:32 PM
· 
Anonymous Jul 24 2026 at 3:32 PM
User information is private
Please provide clarity on the rolling table with drawers for what is desired. A107 for reference item number 83
· 
Jul 27 2026 at 3:52 PM
Escambia County
This table is specified on sheet A103.
62. Door G Jul 27 2026 at 7:57 AM
· 
Anonymous Jul 27 2026 at 7:57 AM
User information is private
The series S2001 called for is automatic. Confirm if this door is to be automatic or manual. 
· 
Jul 28 2026 at 7:50 AM
Escambia County
Per sheet A301 door schedule, this door is to be manual operation.
63. No subject Jul 27 2026 at 3:14 PM
· 
Anonymous Jul 27 2026 at 3:14 PM
User information is private
please clarify all insurance limits for umbrella and BR
· 
Jul 27 2026 at 3:52 PM
Escambia County
This information is available in Sections 7, 8 and 9 of the solicitation.
64. No subject Jul 27 2026 at 9:56 PM
· 
Anonymous Jul 27 2026 at 9:56 PM
User information is private
Will contractor be allowed to discharge ground water into the pond on this parcel for dewatering?
· 
Jul 28 2026 at 9:14 AM
Escambia County
Question is acknowledged and will be addressed.
65. No subject Jul 27 2026 at 9:56 PM
· 
Anonymous Jul 27 2026 at 9:56 PM
User information is private
Sheet C-301 – What elevation will the 42" jack and bore casing under Bauer road need to be and are there any details on how the 14x23 ercp will need to be installed in the round casing? Will there need to be grout filling to provide adequate support of the ercp?
· Question is acknowledged
66. Fire alarm spec Jul 28 2026 at 1:46 PM
· 
Joshua Owens Jul 28 2026 at 1:46 PM
GSI Construction Corporation, Inc
Your information is only visible to you
The attached fire alarm specs call for EST, Notifier, Siemens, and Simplex. Will Potter, FireLite, or Silent Knight be permitted?
· 
Aug 3 2026 at 12:53 PM
Escambia County
Question is acknowledged.
67. Door Type J Aug 3 2026 at 12:39 PM
· 
Anonymous Aug 3 2026 at 12:39 PM
User information is private
Can you please ask the Architect of Record to Verify the RFI’s below, regarding the Sectional Overhead Doors Type J: #1) Does Door Type J require “Water Infiltration Resistance” per ASTM E331 & ASTM E547? The Manufacturers Specified in 08 36 13, Sectional Overhead Doors, are NOT CERTIFIED with the N.F.R.C. for the Air Infiltration, ASTM E283, Florida Energy Code Compliant. Other manufacturers have tested and have an Air Infiltration Rating however they are not N.F.R.C. Rated, we hold the patent. We encourage the GC and Architect of Record to visit the NRFC website directly to verify certification and label requirements according to the N.F.R.C. N.F.R.C. Verification Directions and FL IECC Code Compliance Law attached. Fenestration Products (Doors & Windows) Must Pass (3) Steps: #1) Testing, #2) Certification, #3) Then Provide an N.F.R.C. Label; Required to Pass Inspection. All Manufacturers should and must supply their N.F.R.C. Label Per the current Building Code, any exterior door, window, or Fenestration Product that “Seals the Building Envelope”, must meet the State Energy Code requirement; for Air Infiltration, in addition to thermal U-Factor’s. As such, we can provide a “Fully Insulated Frame”, in addition to Insulated Glass, which is tested and certified to the NFRC standard. 
· Question is acknowledged
68. Hardware Aug 3 2026 at 12:59 PM
· 
Anonymous Aug 3 2026 at 12:59 PM
User information is private
We sent this to the architect directly but wanted to make sure it also came through the GC to ensure it is confirmed and coordinated. Spec section 08 71 00 The hardware specifications listed only ASSA ABLOY brands for each product category, indicating that ASSA ABLOY manufacturing group’s hardware items are all that are approved - sole source – with no reference to acceptable alternative hardware manufacturing groups like ALLEGION, DORMAKABA or HAGER. Division 1 also implies that no substitution would be permitted per page 016000-4, section 2.1, B, paragraph 2. It is our understanding that Escambia County Government projects encourage, perhaps even mandate, competition from other manufacturers/manufacturing groups to help them get the best possible prices for products that have long been considered as being equal or better. Were the ASSA manufacturers and products listed in 087100 and in hardware sets intended to be “basis of design”, not sole source? Warren Door has provided material for several Escambia County fire stations over the last 41 years doing business in Escambia County, with the most recent using ALLEGION, DORMAKABA and HAGER product brands Best, Schlage, Falcon, LCN, Precision, Von Duprin and Hager/Roton. Please advise us of substitution procedures or please review the provided list of manufacturers/materials that we have attached are acceptable. - Hanging Devices: DORMAKABA (BestHI), ALLEGION and HAGER in addition to ASSA ABLOY’s brands Mckinney and Pemko - Mortise locks, power transfers, exit devices, door closers, wiring harnesses: ALLEGION (Falcon, Schlage, Ives, LCN, Von Duprin) and DORMAKABA (BEST, Dorma, Precision, Dorma Commercial) brands in addition to ASSA ABLOY’s brands McKinney, Corbin Russwin, Norton Rixon, Sargent, Accentra (Yale), Adams Rite. - Protective Plates, Operating Trim (push/pulls, kick/mop plates, stops, etc): Burns Manufacturing and ALLEGION (Ives) in addition to ASSA ABLOY brand Rockwood. - Accessories/Barrier Products (thresholds, weatherstrip, saddles): NGP, Hager and Zero in addition to ASSA ABLOY’s Pemko. 
· Question is acknowledged

